Yes. Your instinct is correct.

The code runs, but I would not yet call this a defensible model of a real Sri Lankan CEB LV feeder. It is better described as a first prototype / synthetic feeder model. Before you use it to generate training data for Component 3, we should stop and validate the physical assumptions.

I checked current CEB material as part of this assessment. There is useful evidence available: CEB documentation identifies 11 kV/400 V distribution substations, and CEB material describes retail supply at 400 V three-phase or 230 V single-phase. There are also CEB documents containing actual 160 kVA transformer specifications, including 11/0.4 kV examples.

So the overall direction is plausible, but many individual numbers and modeling choices in your code are not yet sufficiently justified.

First: your code has a serious conceptual problem

You currently have:

11 kV

│

Transformer

│

0.4 kV

│

Pole 1

│

Pole 2

│

Pole 3

│

Houses

That part is reasonable as a simplified radial LV feeder.

But you've mixed together:

- real CEB facts

- engineering assumptions

- invented geographic coordinates

- assumed household loads

- assumed PV capacities

- assumed cable characteristics

- assumed inverter reactive-power behavior

- assumed voltage limits

- assumed transformer short-circuit parameters

and treated almost all of them as if they were established CEB parameters.

That's what we need to fix.

1. What you got right

There are several things I actually like about your model.

11 kV → 0.4 kV

This is defensible.

CEB's distribution documentation identifies 11 kV/400 V distribution substations, while CEB's system documentation also describes customer supply at 400 V three-phase / 230 V single-phase.

So:

b1 = pp.create_bus(net, vn_kv=11.0)

b2 = pp.create_bus(net, vn_kv=0.4)

is a reasonable starting point.

50 Hz

Correct for Sri Lanka.

160 kVA transformer

This isn't an arbitrary capacity. CEB documents do contain 160 kVA transformer examples. One CEB project document, for example, specifies a 160 kVA, 11/0.4 kV, Dyn11 transformer.

So this:

sn_mva=0.160

vn_hv_kv=11.0

vn_lv_kv=0.4

vector_group="Dyn11"

has a defensible starting basis.

But we still need to establish whether 160 kVA is the right transformer for the particular feeder scenario we're modeling.

2. Your biggest problem: the model is not actually modeling the household voltage you care about

Your project is ultimately concerned with something like:

230 V household supply

↓

PV export

↓

voltage rise

↓

maximum allowable PV

↓

hosting capacity

But your entire household network is modeled as:

vn_kv=0.4

That's not necessarily wrong—because the LV distribution network is 400 V line-to-line.

But your eventual voltage constraint needs to be explicitly related to the 230 V phase-neutral customer voltage, or to an equivalent three-phase voltage representation.

You cannot simply say:

max_vm_pu=1.06

and then claim:

"The voltage cannot exceed 240 V."

Those aren't automatically equivalent.

For example:

So if your reference is 230 V:

But we need to establish which CEB/PQCS/solar-inverter voltage requirement applies to your exact study, rather than selecting 1.06 because it looks reasonable.

CEB currently publishes recommended settings for RTSPV inverters, so we should use the actual applicable document rather than inventing the PV voltage limits.

3. Your external grid is currently behaving strangely

Look at this:

External Grid:

p_mw = -0.000134 MW

That's:

So your model is exporting approximately 134 W to the upstream grid.

That's actually consistent with:

PV = 12 kW

Load = 11 kW

roughly giving:

1 kW surplus

although losses/reactive behavior affect the exact number.

So the negative sign itself isn't necessarily a bug.

It means your network is exporting active power toward the external grid.

That is actually the reverse-power-flow phenomenon you're trying to study.

But there's a much bigger issue.

4. Your network is nowhere near a voltage-crisis condition

Your lowest/most relevant bus voltages are approximately:

0.999

1.000

That's essentially nominal.

You have:

12 kW PV

11 kW load

and yet you're seeing almost no voltage rise.

That tells us your feeder has very little voltage sensitivity.

And this is probably because of your line parameters/topology.

Your main feeder has:

45 m

45 m

45 m

and your service drops:

20 m

with a relatively large:

70 mm²

main conductor.

That can make voltage drops/rises very small.

For your research, this is a problem.

Your ML model eventually needs to learn:

grid state

↓

available PV hosting capacity

If almost every scenario gives:

V ≈ 1.000 pu

then your digital twin isn't generating sufficiently informative hosting-capacity boundaries.

5. Your geographic coordinates are not doing what you think

This:

geodata=(6.9271, 79.8612)

does not make your model a real Colombo CEB feeder.

It is only graphical/geographical metadata.

And you've effectively invented a miniature network around Colombo coordinates.

That's fine for visualization.

But it must not be presented as an actual CEB feeder location.

I would rename this conceptually to something like:

Synthetic Sri Lankan LV feeder topology calibrated using publicly available CEB parameters

That is academically much safer.

6. Your "CEB cable" deserves serious investigation

This is one of the biggest things I would stop you on.

You've written:

"CEB_LV_ABC_3x70_54"

and:

r_ohm_per_km = 0.464

x_ohm_per_km = 0.088

max_i_ka = 0.175

and then describe it as:

CEB ABC 70 mm².

But unless you have an actual authoritative specification supporting all of those values, we can't call this a CEB cable model.

Particularly:

R

X

capacitance

ampacity

diameter

emissivity

solar absorptivity

all need appropriate sources.

And there's another problem.

You wrote:

temperature_degree_celsius=80.0

while saying:

temperature corrected for 32°C ambient.

Those are not the same thing.

32°C ambient and 80°C conductor operating temperature are different physical quantities.

So we need to carefully understand Pandapower's temperature correction model before putting both:

r_ohm_per_km = 0.464

and:

temperature_degree_celsius=80

into the same model.

Otherwise we risk double-counting temperature effects.

7. Your service-drop model is particularly questionable

You currently have:

r_ohm_per_km = 1.991

x_ohm_per_km = 0.09

max_i_ka = 0.08

for:

16 mm² service drop

Again, we need an authoritative source.

And more importantly:

Do we actually need to explicitly model every household's service drop?

Possibly yes.

But that should be a deliberate modeling decision.

For hosting capacity, the service connection impedance can matter significantly at the far end.

So this isn't something we should simply invent.

8. Your household loads are not CEB data

This comment:

# Based on CEB consumption data

is too strong.

You have:

House 1 = 1 kW

House 2 = 1 kW

House 3 = 1.5 kW

House 4 = 1.5 kW

House 5 = 1.5 kW

House 6 = 2.5 kW

House 7 = 2.5 kW

These are your assumed operating-point loads, unless you have a dataset that specifically supports these values.

And this:

32% <30kWh

48% 31-90kWh

...

doesn't directly justify:

1 kW

1.5 kW

2.5 kW

Those are different things.

Monthly energy consumption:

is not equivalent to instantaneous demand:

To derive realistic household demand profiles, we'd ideally use an actual time-series dataset and construct:

Household

↓

time

↓

P(t)

Q(t)

rather than manually assigning seven static values.

And this is actually going to help you later when generating your ML training dataset.

9. Your PV model has an important issue

You wrote:

q_mvar=0.00066

for 2 kW PV and say:

0.95 overexcited (Q injection)

You need to be extremely careful here.

You are effectively assuming:

PV generates P

PV also injects Q

with a fixed power factor.

But your research question is about active power hosting capacity.

If your baseline PV inverter has Volt-Var / Volt-Watt functionality or a prescribed reactive-power control mode, that needs to be explicitly modeled and justified.

Otherwise your model can artificially improve voltage conditions.

You could be unintentionally doing this:

PV export ↑

↓

Voltage should rise

↓

But your inverter injects reactive support

↓

Voltage behavior changes

↓

Hosting capacity increases

That may be a valid experiment if your research explicitly studies that inverter control mode.

But your Component 3 currently isn't about inverter Volt-Var optimization.

Therefore I'd initially make the baseline model simpler and establish:

unity-power-factor PV active-power injection

Then later we can introduce reactive control as a separate scenario if justified.

10. Your current model has 12 buses, not 7

And this is actually okay.

You have:

Bus 0  → 11 kV external

Bus 1  → LV transformer

Bus 2  → Pole 1

Bus 3  → Pole 2

Bus 4  → Pole 3

Bus 5  → House 1

Bus 6  → House 2

Bus 7  → House 3

Bus 8  → House 4

Bus 9  → House 5

Bus 10 → House 6

Bus 11 → House 7

So you've moved from our original five-house abstraction to:

7 households + 3 feeder poles + transformer buses

That's actually potentially better for a feeder study, provided we justify it.

But remember your original TAF specifically says:

HIL environment integrates five ESP32 smart metering nodes representing residential households.

Therefore we need to decide whether:

7 households in digital twin

and:

5 physical ESP32 nodes

is intentional.

If only five households will have physical HIL representation, then the other two could be virtual households.

But we need to explicitly define that architecture.

11. Your model currently doesn't really demonstrate hosting capacity

This is the most important point.

You're currently asking Pandapower:

"What happens when I put today's assumed PV generation into this network?"

But your research question requires something more like:

"What is the maximum additional PV capacity this network can accommodate before violating defined operating constraints?"

Those are very different experiments.

You need to eventually have something like:

PV = 0 kW

↓

run power flow

↓

PV = 1 kW

↓

run power flow

↓

PV = 2 kW

↓

run power flow

↓

...

↓

first constraint violation

↓

Hosting Capacity = previous safe PV capacity

And potentially constraints such as:

Maximum bus voltage

Minimum bus voltage

Transformer loading

Line loading

Reverse power flow

depending on what your research definition establishes.

That algorithm is much more important to your Component 3 than having seven realistic-looking household names.

12. What I think we should do now

I would not continue adding code to this model yet.

Instead, let's turn this into a proper M2 validation exercise.

Phase A — Establish the CEB electrical foundation

We need authoritative evidence for:

✓ nominal frequency

✓ MV distribution voltage

✓ LV distribution voltage

✓ customer voltage

✓ transformer ratings

✓ transformer impedance

✓ transformer vector group

✓ LV feeder construction

✓ conductor types

✓ conductor R/X/current capacity

✓ voltage limits

✓ RTSPV voltage requirements

CEB's own regulatory/publication pages give us several starting points, including its Distribution Code and current RTSPV inverter-setting publication.

Phase B — Define YOUR synthetic feeder

Then explicitly document:

Source-backed parameter

OR

Engineering assumption

OR

Experimental variable

For example:

| Parameter | Status |
| --- | --- |
| 50 Hz | Source-backed |
| 11 kV MV | Source-backed |
| 400 V LV | Source-backed |
| 160 kVA transformer | Source-backed candidate |
| 45 m feeder section | Experimental assumption unless sourced |
| 70 mm² conductor | Must verify |
| 20 m service drop | Experimental assumption |
| 2 kWp PV | Experimental variable |
| 4 kWp PV | Experimental variable |
| 1.5 kW household load | Must derive/justify |
| 32°C | Scenario assumption/data-derived |
| 0.95 PF PV | Must verify/justify |

This will make your thesis much stronger.

13. Then rebuild the network from the bottom up

I recommend:

M2

│

┌─────────▼─────────┐

│ CEB parameters    │

└─────────┬─────────┘

│

11 kV source bus

│

160 kVA transformer

│

400 V LV bus

│

LV feeder topology

│

┌─────────┼─────────┐

│         │         │

H1        H2        H3

│         │         │

H4        H5        ...

│

PVs

│

Load profiles

│

Power flow

│

Voltage validation

│

Reverse-flow validation

│

Hosting-capacity scan

Only after this works should you generate thousands of scenarios for your ML model.

14. One thing your current result actually tells us

Your result:

PV = 12 kW

Load = 11 kW

External grid P ≈ -0.134 kW

is useful.

It tells us:

the network is already capable of exporting power upstream.

So reverse power flow is occurring.

But:

V ≈ 1.000 pu

means:

your current feeder isn't electrically stressed enough to produce the voltage constraint that will determine hosting capacity.

That's exactly the thing we need to investigate.

Your eventual experiment should be able to produce a curve something like:

Voltage

│

1.05│                         /

│                       /

1.04│---------------------/---- voltage limit

│                   /

1.03│                /

│             /

1.02│          /

│       /

1.01│    /

│ /

1.00└────────────────────────────

PV penetration / capacity

↑

Hosting Capacity

That curve is much closer to what Component 3 ultimately needs.

My recommendation: freeze this code as Version 0.1

Don't delete it.

Save it as something like:

ceb_grid_midday_v0_1_prototype.py

because it is valuable as your first working prototype.

But don't use its output as training data.

Our next job should be to perform a parameter-by-parameter forensic review of this model:

- create_empty_network

- buses

- external grid

- transformer

- feeder topology

- cable parameters

- line temperature handling

- household load model

- PV model

- reactive power

- voltage limits

- power-flow results

- hosting-capacity definition

And for every parameter, we'll classify it as:

CEB/official source → literature/standard → engineering assumption → experimental variable.

That is how we get from "a Pandapower model that runs" to "a defensible digital twin suitable for generating ML training data."

And yes, I strongly agree with your concern: don't let us train the ML model until we're confident that the ground-truth digital twin is physically and academically defensible.