## Sheet1
Keyword | Meaning | Units
PV capacity | maximum power output that a specific solar installation (or set of installations) can produce under ideal sunlight conditions. | kW
PV Hosting Capacity (Grid Safety Limit) | maximum total amount of solar PV generation that a distribution network (or a specific transformer) can accommodate without causing operational issues | kW
Key technical Criterias CEB evaluates for Clearance for a Solar Installation | Transformer Capacity Limit (The 75%–100% Rule) | CEB will usually stop approving new applications once total installed solar capacity reaches ~75 kW to 100 kW.
| Sanctioned Demand Cap: | A household cannot install a solar system that exceeds their contract demand (e.g., if a house has a standard 30A single-phase connection, max allowed PV capacity is capped at ~5 kW).
| Phase Imbalance | Single-phase solar inverters connected unevenly across phases ($R, Y, B$) cause excessive neutral currents.
| Voltage Drop / Rise Limits | Application Submitted->Retrieve Line Map & Customer Pole No->Calculate Feeder Impedance (R + jX)->Estimate Max Midday Reverse Power Flow->Calculate Expected Voltage Rise (ΔV ≈ P·R / V)->ΔV within limit?->Approve or not?
| CEB performs a technical assessment of the proposed connection against relevant network constraints and operating requirements before allowing the PV system to be connected. | Constraints: voltage limits, transformer/feeder loading, phase imbalance, protection requirements, power-quality considerations, and the capacity of the local distribution network.
Issues still persisi even CEB perfectly managed LV distribution network based on their pre evaluations beforehand | When thousands of balanced, local LV transformers export power simultaneously during low-demand periods (like holidays), their effects aggregate up through the primary substations into the high-voltage transmission lines.
Loss of Utility Visibility: Because local rooftop solar systems are connected behind domestic meters on low-voltage lines, the National System Control Center in Colombo cannot directly monitor or control their output in real time. From the national control room’s perspective, this output appears as an invisible, unmanageable "negative load."
If other houses are consuming electricity, some of that exported power can be consumed locally first.
net power flow through the transformer depends on the sum of generation and consumption on the LV network.
If there is no other local LV demand, the net real power can flow:
LV → transformer → 11 kV network → upstream network.
Yes, equity and unfairness in solar curtailment are major global challenges in distribution network management.
While utilities frame curtailment as necessary for grid safety, structural and geographical factors make the real-world impact unfair for certain solar homeowners.
Key Forms of "Unfair" Solar Curtailment
1. The "End-of-the-Line" Disadvantage (Geographical Unfairness)
The Mechanism: Voltage rise is mathematically highest at the far end of a distribution feeder.
The Unfairness: If 10 houses along a road have identical 5 kW solar systems, the houses closest to the transformer export power easily because local line voltage stays low. However, the household at the very end of the line sees its voltage rise past the inverter safety threshold ($\sim 253\text{V}$).
The Result: The end-of-line inverter automatically trips and shuts down off-and-on all day. The owner loses power generation income through no fault of their own, while neighbors closer to the transformer generate and sell power without issue.
2. The "First-Come, First-Served" Capacity Lockout
The Mechanism: CEB and global utilities allocate hosting capacity sequentially based on when applications are submitted.
The Unfairness: The first few households on a transformer get full clearance to export maximum solar power. Once the transformer's combined limit (e.g., 75 kW) is reached, late-arriving neighbors are either outright rejected, forced to pay out-of-pocket to upgrade the local line/transformer, or restricted to non-exporting setups.
3. Uncompensated Emergency Curtailment
The Mechanism: During emergency over-generation periods (such as low-demand holidays), grid operators may order solar shutdowns or use automated trip signals.
The Unfairness: Large commercial power plants often receive "capacity payments" or contractual compensation when grid operators tell them to ramp down. Residential rooftop owners on net-accounting contracts receive zero financial compensation for lost solar earnings when asked to switch off their systems.
How Modern Smart Grids Address This
To fix these structural inequalities, researchers and progressive utilities are moving away from fixed tripping limits toward Fair Curtailment Strategies:
Proportional / Dynamic Curtailment: Instead of the last house on the wire taking 100% of the loss by tripping completely, smart inverters slightly throttle back generation (e.g., all 10 houses curtail output by 5% simultaneously using active power curtailment algorithms).
Statutory Grid Upgrades: Regulators increasingly require utilities to invest in voltage-regulating transformers (OLTCs) and grid storage rather than forcing end-of-line consumers to bear the financial burden of weak infrastructure.